## Sheet1
Revision Date: 2-4-13 |  |  |  | BNSF Utility Relocation Matrix
Utility Owner | Contact Info | Plan Symbol | Sheet # (overview plan set) | Type of Facility | Description of Relocation/Issues | Existing centerline (CL) crossing(s) station** | Relocation CL crossing(s) Station** | Station Range of Relocation (if longitudinal or angled transverse alignment) ** | Depth @ RR (future) from track bottom | Relocate schedule (tentative) * | Existing facilities - by Permit or Easement
NuStar Energy - location (1) | Dianne Davis 316-721-7057 dianne.davis@nustarenergy.com | G-HP | 5 | 6" High Pressure (HP) Steel petroleum products pipeline | Relocation includes one proposed RR corridor crossing (north of US 275). Crossing will be approximately 30 ft. below proposed RR tracks, per plan. | 1047+90 | 1058+50 | 1024+10 to 1059+20 | Approx. 30 ft. | Spring 2013 | E
NuStar Energy - location (2) at tie-in east of wye | Dianne Davis 316-721-7057 dianne.davis@nustarenergy.com | G-HP | 5 | 6" HP Steel petroleum products pipeline | Existing encasement beneath existing RR near tie -in (east of wye) may need to be extended and pipe lowered. |  |  |  |  | Spring 2013 | E
Black Hills Energy | Chris Dewey 712-325-3022 chris.dewey@blackhillscorp.com | G4-HP | 2 | 8", 12", 16" steel natural gas pipelines and valve set | Valves are being moved away from proposed RR. Bore 8" line to the south under tracks. New 16" line to the west. Must go under Sanitary Sewer | 1005+60 | 1002+70 and 1005+70 | 1002+40 to 1007+80 | 16" @ 12' 8" @ 25' | Summer/Fall 2013 | E
Black Hills Energy - location (2) at 8th St./ 12th Ave. crossing | Chris Dewey 712-325-3022 chris.dewey@blackhillscorp.com | G | 10 | 2" steel natural gas distribution lines | BHE may disconnect some services in area if no longer needed. | 1508+68, 1510+60
Black Hills Energy - location (3) at 7th St. crossing | Chris Dewey 712-325-3022 chris.dewey@blackhillscorp.com | G | 10 | 16" HP steel natural gas transmission | Existing pipeline is encased beneath existing RR tracks at 7th St. crossing. | 1501+91
Magellan MidStream Partners | Tim Kassen 918-574-7351 tim.kassen@magellanlp.com | G4 | 2 | 4" Steel petroluem products pipeline | Existing pipeline currently not in service. A decision has not yet been made by Magellan whether this pipeline will return to service | 1005+72 |  |  |  |  | Unknown
Buckeye Partners, L.P. | Jason Hupp 610-904-4956 jhupp@buckeye.com | G5 | 2 | 8" HP steel petroluem products pipeline | Willbros Engineering has designed a more perpendicular crossing beneath the proposed RR corridor just east of the tank farm. Top of proposed 8" pipe will be a minimum of 6 ft. below RR corridor ditch grade. | 1008+45 | 1009+77 |  |  | Spring 2013 | E
OneOk Partners | Troy Schuermann 580-395-6329 troy.schuermann@oneok.com | G | 2 | 8" Steel petroleum products pipeline | OneOk is currently discussing their crossing of the proposed RR corridor with BNSF and is hoping to use concrete slab protection to protect the pipeline. No relocation plan submitted to IDOT as of December 2012. | 1011+22 |  |  |  | Spring 2013 | E
City of Council Bluffs Sanitary Sewer - location (1) - wye area north of US 275 (2 locations) | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 6 to 8 | 48" Concrete | Several relocations in the proposed wye area planned to simplify crossings and avoid conflict with proposed RR. Relocated portions are proposed to be 36" PVC pipe. |  | 1070+98 and 1112+68 | 1004+80 to 1083+00 | Approx. 16 to 17' (west) and 10 to 12' (east) top/pipe | Prior to RR grading | E
City of Council Bluffs Sanitary Sewer - location (2) - east end of wye (tie in) | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 9 |  | Existing track crossing alignment to be extended to south and encased beneath proposed RR tracks. Replacement pipe will be 30" PVC at this location. |  |  |  | Approx. 12 to 13" top/pipe | Prior to RR grading
City of Council Bluffs Sanitary Sewer - location (3) near I-29 bridges | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 3 | 48" Concrete | Relocation will eliminate existing crossing in this area. | 1024+26 and 1028+64 | N/A |  | N/A | Prior to RR grading | E
City of Council Bluffs Sanitary Sewer - location (4) - east of tank farm | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 2 | 48" Concrete | Relocation in this area will remove 2 CBEC and 1 BNSF crossing and provide one proposed RR corridor crossing. Relocated portions are proposed to be 48" PVC pipe. | 1001+82 | 1005+58 |  | Approx. 14 to 15' top/pipe | Prior to RR grading | E
City of Council Bluffs Sanitary Sewer - location (5) - 8th St./12th Ave. crossing | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 10 |  |  | 1508+92, 1510+20
City of Council Bluffs Sanitary Sewer - location (6) - existing crossing near RR tie in east of 7th St./13th Ave. | Dave Vermillion 712-328-4635 dvermillion@councilbluffs-ia.gov | San | 10 |  |  | 1500+56
Council Bluffs Water Works - location (1) near I-29 bridges | Brian Cady 712-328-1006 bcady@cbwaterworks.com | W | 3 | 16" Steel water main | Relocating to avoid conflicts with proposed I-29 bridges. Proposed casing will be 30" outside diameter and a minimum 5' cover will be maintained. | 1027+70 | 1030+58 |  |  | Prior to RR Grading | P
Council Bluffs Water Works - location (2) - 8th St./12th Ave. crossing | Brian Cady 712-328-1006 bcady@cbwaterworks.com | W | 10 | 6" and 8" Steel distribution lines | Distribution and several smaller service lines/valves located in 8th St./12th Ave. intersection. | 1508+62, 1510+40
Council Bluffs Water Works - location (2) - 7th St. Crossing | Brian Cady 712-328-1006 bcady@cbwaterworks.com | W | 10 | 8" Steel distribution line | Existing line is encased beneath existing RR tracks at 7th St. crossing. | 1502+45
Iowa DNR Storm Sewer | Dan Jacobs 712-366-0220 daniel.jacobs@dnr.iowa.gov | St.S.2 | 5 | 48" Concrete | Horizontal alignment will not change. The portion beneath the RR ROW will be replaced with 3750 D concrete pipe. | 1054+67 | 1054+67 |  | Approx. 11.4 ft. (top/pipe) | Spring 2013 | E
CenturyLink (local) | Ed Krieger 402-572-5856 edward.krieger@centurylink.com | T1 | 3 | 9-way duct (copper and fiber) | Relocating to avoid conflicts with proposed I-29 bridges. | 1030+70 | 1028+02 | 1026+20 to 1030+26 |  | Spring 2013 | E
CenturyLink (local) - location (2) at 8th St./12th Ave. crossing | Ed Krieger 402-572-5856 edward.krieger@centurylink.com |  | 10 | 6-way duct and buried cable |  | Exact crossing locations to be determined. Facilities present in north ROW of 12th Ave and west ROW's of 7th St. and 8th St.
CenturyLink (long distance) | Bob Sampson 636-887-5367 robert.sampson@centurylink.com | F07 | 5 | Fiber | Joint relocation with INS and LightCore. Relocating to avoid conflicts with US 275 construction. Relocated line will be encased in HDPE conduit. | 1049+78 | 1050+82 |  | Minimum 10' - Fiber will be encased in HDPE ducts. | Spring 2013 | E
LightCore | Bob Sampson 636-887-5367 robert.sampson@centurylink.com | F06 | 5 | Fiber | Relocating to avoid conflicts with I-29 highway construction. Relocated line will be a joint relocation with INS and CenturyLink L.D. on north side of US 275. Existing LightCore fiber in south ROW of US 275 not currently in service. Relocated line will be encased in HDPE conduit. | 1046+27 |  |  |  | Spring 2013 | E
Iowa Network Services (INS) | Jeff Klocko 515-830-0445 JEFF@netins.com | F05 | 5 | Fiber | Joint relocation with CenturyLink L.D. and LightCore. Relocating to avoid conflicts with US 275 construction. Relocated line will be encased in HDPE conduit. | 1049+78 |  |  |  | Spring 2013 | P
Iowa Communications Network (ICN) | Larry Klawitter 515-725-4741 larry.klawitter@iowa.gov | F04 | 3 | Fiber | Relocating to avoid conflicts with I-29 bridge/highway construction. Relocated line will be encased in 2" HPDE duct. | 1028+53 | 1024+79 |  | Variable - minimum 10 to 12 ft. | Spring 2013 | P
MCI | Steve Bonczkowski 630-395-6701 stephen.bonczkowski@verizonbusiness.com | F09 | 4 | Fiber (encased in 4" galv. steel conduit) | No relocation planned to accommodate initial highway grading/bridge projects. | 1046+34 |  |  | N/A | N/A | P
AT&T | P.J. McDermott 816-275-4014 pjmcdermott@att.com | F11 | 4 | 6-way HDPE duct | No relocation planned to accommodate initial highway grading/bridge projects. Existing facilities are approx. 8 ft. below existing ground at proposed BNSF track crossing. | 1046+63 |  |  | N/A | N/A | P
Iowa DOT/City of Council Bluffs | Mike Miller 712-366-0332 michael.miller1@dot.iowa.gov | E2 | 3 | Buried electric distribution line (traffic signal feed) | Existing power feed along I-29 northbound off ramp to US 275 will be abandoned in place. Relocated line will not cross existing RR or proposed RR corridor. | 1027+91 | N/A | N/A | N/A | Spring 2013
MidAmerican Energy (electric) | Tim Theobald 712-366-5668 trtheobald@midamerican.com | E1 | 3 | Overhead electric distribution | Existing overhead 13.2 kv 3 phase crossing over I-29 will be removed to accommodate I-29 bridge/highway construction. | 1028+02 | N/A | N/A | N/A | Spring 2013 | P
* Relocation schedules based on current IDOT project letting schedules as of the date at the top of the page.
**Stationing is approximate and based on proposed BNSF track centerline, per Iowa DOT D5 Railroad plans . IM-029-2(55)49--13-78